REFLUX IT

# Guadeloupe Water Technology and Procurement Study

Low energy capture  desalination  circular recovery  and EU first sourcing

Decision report  •  11 October 2026

Design basis  •  from a few litres per day to emergency service for 8,000 people

|  | The decision in one sentence Build a layered water system: local rain storage and measured fog capture first; passive solar stills for household resilience and demonstration; a modular solar seawater RO plant as the dependable 8,000-person backbone; water storage instead of large batteries; and a controlled REFLUX IT programme that recovers pressure, heat, clean side-streams and selected minerals without pretending brine can circulate forever. |
| --- | --- |

Prepared as a supplier-neutral research and procurement brief

European and Guadeloupe production is preferred through transparent whole-life criteria. Chinese systems remain in the comparison lane and can qualify through the same performance, compliance, service and factory-acceptance gates.

# Executive decision

|  | Recommended backbone For the 8,000-person emergency target, procure three independent 60 m³/day-class solar SWRO trains arranged as two duty plus one standby, or an equivalent 120–150 m³/day modular EU system with service redundancy. Size the operating solar field initially around 90 kWp, confirm auxiliary loads by quote, and store at least 360 m³ of finished water in split cyclone-resilient tanks. |
| --- | --- |

| Layer | What it does | Preferred route | Decision |
| --- | --- | --- | --- |
| 1 Avoid demand | Leak detection low-flow fixtures greywater for non-potable uses | Local plumbing and controls | Do now |
| 2 Capture free water | Roof rain fog drizzle limited dew | Guadeloupe tanks plus FogQuest or CloudFisher pilot | Do now as measured pilots |
| 3 Passive production | Solar distillation without grid power | GWS-1 local build plus Carocell benchmark | Household and contingency only |
| 4 Reliable base load | Potable supply independent of rainfall | EU solar SWRO with pressure-energy recovery | Primary municipal backbone |
| 5 Emergency diversity | Portable manual or DC watermaking | Katadyn and Spectra | Strategic stock |
| 6 Resource recovery | Pressure heat water side-streams salts | REFLUX IT loops with monitoring | Integrate selectively |

## What should not be the backbone

Fog alone is too site-sensitive and cyclone-exposed until a full dry-season and preferably 12-month field dataset exists.

Passive dew is elegant but its normal yield is too low for thousands of people.

Compressor atmospheric water generators are commercially real but use roughly two orders of magnitude more electricity per cubic metre than efficient seawater RO under the compared vendor conditions.

Cloud seeding cannot make water from a clear sky and does not belong in the committed supply budget for Guadeloupe.

## Design basis

| Service level | Per person | 8,000 people | Use in this study |
| --- | --- | --- | --- |
| Drinking only | 3 L/day | 24 m³/day | Minimum beverage volume |
| Drinking and basic cooking | 5 L/day | 40 m³/day | Short disruption target |
| Emergency basic service | 15 L/day | 120 m³/day | Primary plant design point |
| Reduced domestic service | 50 L/day | 400 m³/day | Future expansion not initial scope |
| Typical higher domestic service | 100 L/day | 800 m³/day | Network-scale planning only |

The 15 L/person/day benchmark is an emergency minimum, not a normal long-term standard of living. WHO materials use 15 L/person/day as a minimum quantity to reach quickly after an emergency; actual design must include institutions, losses, firefighting and vulnerable users. [1]

# Guadeloupe design envelope

Guadeloupe is not uniformly wet. Normal annual rainfall ranges from about 600 mm in the driest areas to almost 6,200 mm near La Soufrière. Windward Basse-Terre benefits from moist trade winds lifted by the mountains, while Grande-Terre and the smaller low-relief islands face more recurrent drought. This spatial contrast is the reason to combine catchment, storage and seawater treatment rather than assume that high island-wide humidity equals reliable local yield. [2]

| Hazard or condition | Design response |
| --- | --- |
| Cyclones and extreme gusts | Fog mesh must lower or detach rapidly; still glass must be removable; containers and PV structures require engineered anchoring; tanks should be buried or bermed where feasible. |
| Salt air and UV | Specify marine-grade 316L in wetted metal paths, UV-stabilised polymers, replaceable fasteners and coatings, and a spares strategy. |
| Sargassum and coastal organics | Prefer screened offshore or beach-well intake after hydrogeology; otherwise include robust screening, clarification or flotation and UF as site tests dictate. |
| Dry season and rainfall volatility | Store water rather than electrons, diversify sources and size the RO base load to the dry-season requirement. |
| Warm humid air | Helpful to condensation AWG output, but not enough to overcome the technology's high electricity intensity at municipal scale. |
| Power interruptions | Operate PV-direct in daylight, use gravity distribution and reserve grid or wind generation for essential pumps, controls, disinfection and night demand. |

## Cyclone operating mode

1.  At alert level, lower fog meshes, remove solar-still glazing, isolate tanks and protect vents and overflow points.

2.  Before landfall, fill treated-water storage and chemically verify disinfectant residual.

3.  After the storm, quarantine all raw capture until turbidity, conductivity and microbiology pass release criteria.

4.  Restart the intake and RO in a staged sequence after inspecting screens, membranes, dosing and brine discharge.

# Technology ranking and scale

| Technology | Typical output basis | Power | Best scale | Guadeloupe verdict |
| --- | --- | --- | --- | --- |
| Roof rain | Annual rainfall × area × runoff coefficient | None gravity possible | All | First capture layer storage dominates |
| Fog mesh | Often 3–10 L/m²/day annual project average highly local | None | Pilot to village | Promising windward sites measure first |
| Passive dew | About 0.3–0.6 L/m²/day in favourable literature | None | Device and garden | Useful supplement not bulk supply |
| GWS-1 solar still | 2.5–4 L/m²/day design basis | None | Household | Local resilience and training platform |
| Commercial solar still | Vendor claims vary require local seawater test | None | Household to small cluster | Benchmark GWS-1 against one purchased unit |
| Manual RO | About 4.5 L/hour for Katadyn Survivor 35 | Human power | Liferaft and emergency | Stock for clinics and response teams |
| Solar DC RO | 30–64 L/hour examples | About 110 W class at low end | Household to small village | Strong emergency option |
| Solar SWRO | 1–10,000 m³/day vendor range | About 2.5 kWh/m³ RO core claim | Village to municipal | Best dependable backbone |
| Condensation AWG | 52–5,091 L/day EU models | About 0.22–0.42 kWh/L | Point or emergency | Niche only avoid bulk deployment |
| Membrane distillation | Project-specific | Low-grade heat plus pumps | Brine side-stream | Pilot for recovery not base load |

Area comparison uses 120 m³/day. Rain assumes runoff coefficient 0.8 and annual averages of 1.4 or 3.0 m. Fog, dew and still ranges are indicative; local meteorology and downtime control the actual result.

## Scale snapshots

| Tier | Demand example | Practical package |
| --- | --- | --- |
| Micro | 3–75 L/day | One GWS-1 or commercial still; roof capture and 1–5 m³ tank; manual RO for survival backup. |
| Small community | 0.5–7.5 m³/day | Rain storage plus measured fog array; 5 m³/day skid SWRO; one spare high-pressure pump and membrane set. |
| Medium community | 15–40 m³/day | Two modular solar SWRO trains; 45–120 m³ treated storage; local rain and fog offset. |
| 8,000-person emergency | 120 m³/day | Three 60 m³/day-class trains two duty plus one standby; about 90 kWp operational PV design basis; 360 m³ split storage. |
| Future domestic expansion | 400–800 m³/day | Network planning multiple larger trains expanded intake and brine study demand reduction first. |

# Fog capture

Fog collection is passive impaction, not refrigeration. Wind carries liquid droplets into a double layer of correctly selected mesh; droplets coalesce, drain to a gutter and move by gravity. FogQuest states that its process needs no generator and uses 35 percent shade-coefficient UV-protected Raschel mesh in a double layer. Its commonly cited 40 m² collector average is about 200 L/day, but site output varies sharply and their figures should be treated as feasibility values rather than a Guadeloupe guarantee. [3]

| Ready route | Origin | Format | How to buy | Important limit |
| --- | --- | --- | --- | --- |
| FogQuest | Canada NGO mesh sourced in Chile | 1 m² standard test and 40 m² large collector methodology | Project engagement and field siting support | Best used for measurement-led community projects |
| CloudFisher by Aqualonis | Germany | Test unit Mini about 18 m² Pro about 54 m² | Direct manufacturer quote with site support | Published wind resistance around 120 km/h is below major Guadeloupe cyclone gusts lower or remove |
| KnitMesh Technologies | United Kingdom | Engineered knitted-wire fog media | Direct industrial enquiry | Specify potable-contact path corrosion and collection test |
| Local fabricated SFC | Guadeloupe plus EU components | 1 m² test frame with calibrated gauge | Local metalwork and plumbing contractor | Use the standard geometry to preserve comparability |

## Fog pilot specification

Install at least six 1 m² standard fog collectors across windward Basse-Terre elevations, each with an adjacent rain gauge and weather logger.

Record litres per square metre per day, wind speed and direction, relative humidity, rainfall, conductivity, turbidity, pH and microbiology.

Run for 12 months where possible and include the complete dry season before any large collector purchase.

Use quick-release mesh and a documented cyclone lowering drill; do not leave a 120 km/h-rated collector exposed to Category 4 conditions.

Treat fog water as raw water until the complete catchment, storage and disinfection train is validated.

## What fog can realistically supply

At 3–10 L/m²/day, a 54 m² collector would average roughly 162–540 L/day before downtime and treatment losses. Reaching 120 m³/day would require about 12,000–40,000 m² of effective mesh. That is why fog is a valuable offset and remote-site technology, not the unmeasured foundation of the 8,000-person promise.

# Rain and dew capture

Rainwater should be the first harvested resource because roofs already exist and local tanks and installers are available. At 1,400 mm/year and an 0.8 runoff coefficient, each square metre yields about 1,120 L/year, or 3.1 L/day averaged across the year. At 3,000 mm/year it yields about 2,400 L/year, or 6.6 L/day. The constraint is dry-season storage and sanitary separation, not annual arithmetic.

| Supplier or route | Origin | Available offer | Procurement note |
| --- | --- | --- | --- |
| PROCAP | Guadeloupe and Antilles | Rotomoulded PE tanks including ACS potable-water models | Strong local-production preference specify whether the tank is approved for potable storage or only rainwater/non-potable use |
| Bèl Lapli | Guadeloupe | Turnkey rainwater tanks and treatment | Ask for exact treatment barrier commissioning tests and ARS-compatible use case |
| Soley K'raïb | Guadeloupe | Tank supply and installation | Confirm current aid eligibility and minimum capacity before relying on subsidy |
| PAK971 | Guadeloupe | ACS tank range reported from 300 to 9,500 L | Useful modular household route obtain written potable-contact documentation |
| GRAF Carat XL | Germany | 10,000 L buried tank through French distribution | EU benchmark freight and cyclone-grade installation extra |

|  | Connection rule Keep harvested rainwater physically separated from the public potable network unless an approved backflow-protected arrangement is designed. Use first-flush diversion, screened inlets, opaque tanks, accessible cleaning, protected vents, filtration and disinfection appropriate to the intended use. |
| --- | --- |

## Passive dew

Radiative dew collectors cool a surface below the dew point at night. Literature values around 0.3–0.6 L/m²/day make them suitable for demonstration, plant irrigation and small emergency volumes. At the 120 m³/day target, they imply roughly 200,000–400,000 m² of collector. Sorbent and hydrogel systems can work at lower humidity but require heat for regeneration; most high-performing examples remain research rather than supported turnkey products.

# Passive solar desalination

## GWS-1 local build

The existing GWS-1 design is a 1 m² single-basin passive solar still intended for Guadeloupe fabrication. It uses a local fired-clay or chamotte shell, a 316L basin and gutter, two removable tempered-glass panes at about 12 degrees and food-grade elastomers. Its design basis is 2.5–4 L/day typical, with 5 L/day as a favourable upper value. It needs no pump, pressure or electricity.

| Item | GWS-1 specification | Procurement implication |
| --- | --- | --- |
| Footprint | Outer body about 1.12 × 1.12 m basin 1.00 × 1.00 × 0.035 m | Local mould masonry and metalwork are feasible |
| Glazing | Two panes around 525 × 1,080 mm 4–6 mm tempered | Removable before cyclone hold protected spares |
| Feed | 8–12 L seawater batch | Manual filling possible source-screen and avoid fuel contamination |
| Output | 2.5–4 L/day typical design basis | Pilot against local weather and seawater before scale claims |
| Product finish | Distillate | Remineralise disinfect and store in ACS-compliant container |
| Cleaning | Drainable shallow tray | Plan salt removal and acid cleaning procedure recover salt only after quality analysis |

For drinking-only supply of 24 m³/day, GWS-1 requires about 6,000–9,600 modules at 4–2.5 L/day. For the 120 m³/day emergency service target, it requires about 30,000–48,000 modules. It is therefore a household resilience product and local manufacturing programme, not the municipal base load.

## Already assembled solar still

| Supplier | Origin | Offer | Evidence gate |
| --- | --- | --- | --- |
| F Cubed Carocell | Australia with international projects | Modular direct solar desalination panels | Current vendor material claims roughly 25 L/day for a panel in one project context while older brochures cited about 10–15 L/day for 2–3 m² models. Buy one benchmark only after a guaranteed Guadeloupe seawater curve and potable-path documentation. |
| Desolenator | Netherlands and international | Current offer is large solar thermal multi-effect and mechanical-vapour-compression infrastructure | Treat as custom large-project enquiry not a current household still kit. |

|  | Water quality warning Solar distillation removes salts but some volatile contaminants can carry over. Do not feed seawater contaminated with fuel, solvents or severe algal decay without source control and testing. Distillate also needs stabilisation or remineralisation before distribution to reduce corrosivity and improve taste. [4] |
| --- | --- |

# Low energy reverse osmosis

Seawater reverse osmosis is the most mature dependable route from tens of litres to thousands of cubic metres per day. The low-energy step is not a magic membrane: it is pressure-energy recovery, efficient pumps, sound intake pretreatment and operating the plant near its design point. Water storage can replace most electrical battery storage by running hard in daylight and delivering by gravity around the clock.

## Small and portable systems

| Supplier and model | Origin | Nominal output | Power and role | Buy route |
| --- | --- | --- | --- | --- |
| Katadyn Survivor 06 | Switzerland | Emergency survival unit 1–6 people | Manual | Katadyn marine and safety dealer network |
| Katadyn Survivor 35 | Switzerland | About 4.5 L/hour vendor daily figure 132 L | Manual clinics and liferafts | Katadyn marine and safety dealer network |
| Spectra Aquifer 200 | United States | About 30 L/hour | 12 or 24 V DC about 110 W energy-recovery pump | Spectra authorised distributor |
| Spectra Aquifer 360 | United States | About 57 L/hour | 12 or 24 V DC solar or wind compatible | Spectra authorised distributor |
| Spectra LB400 | United States | About 64 L/hour up to 12 hours/day | DC with Clark energy recovery | Spectra authorised distributor |
| Rainman portable | Australia with EU dealers | Model-dependent roughly 100–240 L/hour in larger AC packages | Transportable backup generally higher energy than Clark-type recovery | European marine dealer network |

## Medium and large solar SWRO

| Supplier | Origin | Commercial range | Why shortlist | Qualification point |
| --- | --- | --- | --- | --- |
| OSMOSUN | France | About 1–10,000 m³/day SWRO modular combinations higher | Battery-free solar operation EU service path published 2.5 kWh/m³ core at 35 g/L | Reconcile guaranteed daily output PV area auxiliaries intake and brine scope in one performance schedule |
| Elemental Water Makers | Netherlands | About 5–100 m³/day standard project bands | Solar RO with energy recovery current indicative complete-project bands published | Quote Guadeloupe freight civil work pretreatment and long-term service |
| Solar Water Solutions | Finland | About 1–1,000 m³/day cited range | Renewable-compatible desalination packages | Demand references in tropical seawater and cyclone installation design |
| Boreal Light Winture | Germany | About 1–30 m³/hour product family | Large solar water systems with project delivery | Confirm seawater configuration whole-plant SEC and Caribbean spares |
| GivePower | United States nonprofit | Solar water farm projects about 15,000–75,000 L/day | Potential humanitarian partner | Partnership route rather than ordinary equipment purchase |

Comparison uses OSMOSUN's published 2.5 kWh/m³ RO-core figure at 35 g/L and GENAQ Nimbus N4500's 0.22 kWh/L, equivalent to 220 kWh/m³. Fog and passive stills use no operating electricity but require large collection area. Vendor conditions differ; this chart is a screening comparison, not a tender guarantee. [5] [6]

## Recommended 8,000-person configuration

1.  Commission raw-seawater analysis over seasons, including algae, hydrocarbons, turbidity, temperature, boron and sargassum-related risk.

2.  Tender three independent 60 m³/day-class trains with two duty plus one standby, or an equivalent N+1 arrangement delivering 120 m³/day under the guaranteed worst design condition.

3.  Use pressure exchangers or equivalent high-efficiency recovery and require measured whole-plant specific energy, including intake, pretreatment, dosing, post-treatment and controls.

4.  Use about 90 kWp as the first-pass PV sizing basis for 120 m³/day from OSMOSUN's 0.75 kWp per daily m³ rule, then add the supplier's documented allowance for losses and auxiliaries. [5]

5.  Store 360 m³ finished water as a three-day emergency reserve, split into isolated tanks such as six 60 m³ cells or twelve 30 m³ cells.

6.  Finish with remineralisation, pH stabilisation, disinfection, online conductivity and turbidity, secure sampling points and an operator laboratory plan.

|  | Illustrative brine balance At an assumed 40 percent recovery, 120 m³/day of product needs about 300 m³/day feed and leaves about 180 m³/day concentrate. Starting from 35 g/L seawater, the concentrate is roughly 58 g/L before detailed ion and temperature effects. Pressure-energy recovery reduces electricity; it does not recover this water or remove the salt. |
| --- | --- |

# Desert water technologies

Desert water technology is a family, not one product. The relevant question is which source is already present: liquid fog, night-sky cooling potential, humidity that can be condensed, saline groundwater, seawater or low-grade heat. Guadeloupe has abundant seawater and pockets of orographic fog, so it should borrow the best desert techniques without copying the wrong energy economics.

| Method | Maturity | Energy input | Guadeloupe use |
| --- | --- | --- | --- |
| Fog mesh | Commercial and community proven | Wind and gravity | Mountain pilot and remote supply |
| Radiative dew | Field-demonstrated at small scale | Night-sky cooling | Supplementary education agriculture |
| Compressor AWG | Commercial | High electricity | Point-of-use emergency or bottled-water displacement only |
| Desiccant or hydrogel AWG | Fast-moving research and early products | Solar or waste heat regeneration plus fans | Monitor do not count in current supply |
| Solar still | Mature simple principle | Sunlight | Household resilience and local manufacture |
| PV-driven SWRO | Commercial and scalable | Solar electricity with pressure recovery | Primary bulk-water choice |
| Membrane distillation | Commercial niches and pilots | Low-grade heat plus pumping | Brine concentration and waste-heat recovery pilot |

## Atmospheric water generators

| Supplier | Origin | Example | Output and energy | Decision |
| --- | --- | --- | --- | --- |
| GENAQ | Spain | Nimbus N500 | 506 L/day 0.24 kWh/L | EU-first emergency pilot |
| GENAQ | Spain | Nimbus N4500 | 4,445 L/day 0.22 kWh/L | Not bulk due to energy |
| GENAQ | Spain | Cumulus C5000 | 5,091 L/day 0.26 kWh/L | Mobile emergency niche |
| Watergen | Israel | GEN-M Pro and GEN-L | Up to about 1,000 and 6,000 L/day vendor ratings | Non-EU comparison verify climate curve |
| Heaven Springs or FND | China | Industrial AWG | Vendor family around 500–5,000 L/day | China benchmark lane full FAT and potable compliance |
| SOURCE Hydropanel | United States | Self-contained solar panel | A few litres/day class | Remote point use not municipal |

At 0.22 kWh/L, producing 120 m³/day requires about 26,400 kWh/day. The RO-core comparison at 2.5 kWh/m³ is about 300 kWh/day, before common intake and finishing loads. Even allowing for different boundaries, AWG is not a rational bulk substitute when seawater is beside the site.

# REFLUX IT recovery architecture

REFLUX IT should mean measured recirculation with a defined contaminant boundary. Every loop must state what is recovered, what accumulates and where the final reject goes. The objective is fewer imported kilowatt-hours, fewer litres of new feed, longer component life and useful co-products without compromising drinking-water safety.

| Loop | Capture | Return path | Control boundary | Priority |
| --- | --- | --- | --- | --- |
| Pressure reflux | Hydraulic pressure in RO brine | Isobaric pressure exchanger or Clark-type pump to incoming feed | No mixing claim beyond device specification monitor SEC and leakage | Immediate |
| Heat reflux | RO motor heat AWG condenser heat solar PVT heat | Feed preheat where useful hot water membrane-distillation side-stream | Avoid heating RO feed beyond membrane design legionella controls on warm water | Pilot |
| Clean-water reflux | Final rinse safe backwash supernatant HVAC condensate | Earlier treatment stage or non-potable tank | Never return chemicals or pathogens without hazard review | Immediate after validation |
| Rain fog dew merge | Multiple low-energy raw sources | Common equalisation then source-appropriate treatment | Online conductivity and turbidity isolate suspect source | Immediate |
| Brine water reflux | Residual water in concentrate | Second-pass RO or membrane distillation | Scaling and osmotic pressure increase each cycle fixed maximum concentration | Pilot only |
| Mineral reflux | Salt-rich concentrate | Crystallisation or sale/use after analysis | Heavy metals antiscalant and market quality no food claim without certification | Research |
| Storage reflux | Daytime solar surplus as treated water | Elevated or pressure-managed tanks feed night demand | Maintain disinfectant residual and turnover | Immediate |
| Material reflux | Local clay shell repairable steel replaceable mesh | Repair and reuse programmes | Potable-contact parts remain compliant | Immediate |

|  | The non-negotiable limit A closed brine loop is not perpetual water reuse. Salt, boron, antiscalant and trace contaminants accumulate while osmotic pressure rises. The system needs a licensed terminal pathway: a designed marine diffuser, a validated salt or mineral product, evaporation or a true zero-liquid-discharge train. Energy recovery alone is not water recovery. |
| --- | --- |

## Practical process train

| Stage | Equipment | Recovered output |
| --- | --- | --- |
| Capture | Rain roofs fog mesh seawater intake | Gravity-fed raw water where terrain permits |
| Pretreatment | Screens settling or flotation media or UF dosing | Backwash supernatant only if validated for return |
| Primary separation | SWRO with isobaric ERD | Brine pressure returned to feed |
| Product finish | Calcite or controlled remineralisation disinfection | Stable potable water |
| Storage | Split buried or anchored tanks | Energy stored as water gravity delivery |
| Concentrate side-stream | Optional MD or crystallisation pilot | Additional water salt or mineral sample data |

# EU first supplier strategy

An EU-first result can be achieved without an origin-only exclusion. Score whole-life performance that matters in Guadeloupe: potable compliance, independently witnessed output, energy at the stated seawater condition, cyclone design, repair time, local training, spare parts held in the EU or Caribbean, warranty response and transparent end-of-life handling. If public money is involved, have the contracting authority confirm the applicable French and EU procurement route. The European Commission notes that lifecycle-cost methods and tenderer data requirements should be disclosed in the procurement documents. [7]

| Evaluation criterion | Weight | Evidence required |
| --- | --- | --- |
| Potable water and materials compliance | 25 | EU drinking-water basis ACS or equivalent potable-contact dossier lab plan |
| Guaranteed output under Guadeloupe conditions | 20 | 35–40 g/L warm seawater site solar profile turndown and availability |
| Whole-plant energy and REFLUX recovery | 15 | kWh/m³ including auxiliaries ERD efficiency measured acceptance test |
| Cyclone and corrosion resilience | 15 | Structural calculations anchoring marine coatings safe shutdown procedure |
| Service spares and training | 10 | Response time EU or Caribbean stock French manuals operator course |
| Lifecycle cost | 10 | 20-year NPV assumptions disclosed chemicals membranes energy disposal |
| Circularity and local value | 5 | Repairability local fabrication share take-back and material recovery |

## Current buy and quote matrix

| Need | EU or local lead | Non-EU comparison | Procurement action |
| --- | --- | --- | --- |
| Rain storage | PROCAP Bèl Lapli Soley K'raïb PAK971 GRAF | Chinese tanks only if freight and ACS-equivalent dossier justify | Buy locally after civil and potable-use check |
| Fog pilot | CloudFisher Germany KnitMesh UK local SFC fabrication | FogQuest Canada and Chile mesh | Buy six standard collectors not a production field yet |
| Passive solar still | GWS-1 Guadeloupe build | Carocell Australia benchmark | Build twelve GWS-1 and buy one comparator |
| Manual emergency RO | Katadyn Switzerland | Other marine units only after service and parts check | Buy for clinics shelters and response teams |
| Small solar DC RO | No stronger EU low-power household comparator identified | Spectra USA | Buy one field unit and retain full spares |
| 120 m³/day solar SWRO | OSMOSUN France lead Elemental Netherlands Solar Water Solutions Finland B and P Italy | FHNED Wangyang Hexing China | Two-stage tender with witnessed FAT and lifecycle scoring |
| AWG emergency | GENAQ Spain | Watergen Israel FND or Heaven Springs China | Pilot only if a specific resilient use case exists |
| Brine recovery pilot | RN Solutions Netherlands memsys Germany Salinity Solutions UK for suitable feed | Chinese MD or crystalliser only after references and lab test | Treat as R&D side-stream not a prerequisite for water supply |

## Budget anchors not quotations

| Item | Published screening figure | How to use it |
| --- | --- | --- |
| FogQuest standard test collector | US $75–200 each to build | Legacy public budget basis confirm current mesh labour freight and expert siting |
| FogQuest 40 m² large collector | US $1,000–1,500 each about 10-year life stated | Legacy public budget basis excludes cyclone adaptation tanks and treatment |
| Elemental 5,000–11,000 L/day project | About €40,000–€70,000 indicative | 2026 online screening range confirm complete Guadeloupe scope |
| Elemental 20,000–40,000 L/day project | About €100,000–€120,000 indicative | Use only to sanity-check bids not an award price |
| Elemental 50,000–100,000 L/day project | About €190,000–€450,000 indicative | Wide site-dependent band 120 m³/day plus N+1 and storage will be higher |
| GRAF Carat XL 10,000 L tank | French listing around €6,002 TTC | Tank only benchmark Guadeloupe freight excavation anchoring pipework and treatment extra |

## China comparison lane

China has deep capability in membranes, pressure vessels, pumps, desalination integration, solar equipment and atmospheric water generation. Including it strengthens the competition. The fair approach is the same pass-fail gate for every origin, with extra document and service checks where the supplier lacks an established EU support chain.

| Chinese supplier | Visible offer | Why compare | Mandatory gate before award |
| --- | --- | --- | --- |
| FHNED Jiangsu Fenghai | 5 15 25 50 100 and 144 m³/day SWRO listings including new-energy container models | Direct size match around the project target | Third-party FAT full bill of materials CE dossier potable-contact declarations 35 g/L performance EU spares and commissioning partner |
| Zhuhai Wangyang | Container SWRO examples around 65 144 500 and 720 t/day optional ERD | Broad maritime track record claim | Guaranteed whole-plant SEC boron and chloride reference calls cyber and controls documentation |
| Hexing | Factory-integrated container SWRO with solar and storage compatibility | Potential fast deployment | Clarify whether PV batteries intake post-treatment and brine outfall are included |
| Snowate | iERD pressure exchanger and water-treatment components | Component-level cost and technology benchmark | Independent efficiency curve seawater materials endurance test leakage and warranty |
| FND or Heaven Springs | Atmospheric water generators up to several thousand L/day | Useful AWG price-performance comparison | Output curve at Guadeloupe temperature and RH kWh/L noise refrigerant sanitation and EU potable compliance |

## Factory acceptance test essentials

Witness 72 continuous hours at agreed feed salinity, temperature and fouling index; do not accept a freshwater recirculation demonstration.

Record product flow, salt rejection, boron where applicable, recovery, pressure, chemical use, noise and whole-plant kWh/m³.

Verify every major component serial number against the approved bill of materials and retain PLC source backup and passwords.

Take accredited laboratory samples and define rejection and liquidated-damages thresholds in the contract.

Ship commissioning spares, two years of critical consumables, French maintenance instructions and operator training with the plant.

Hold final payment until site acceptance under Guadeloupe feed and solar conditions.

# Cloud seeding reality check

|  | Short answer The material normally meant is silver iodide AgI not silver chloride. Glaciogenic seeding targets suitable supercooled clouds; hygroscopic seeding generally uses salts in warm clouds. Rockets are only delivery systems. Seeding cannot create clouds or moisture. |
| --- | --- |

WMO distinguishes hygroscopic methods that modify liquid drops from glaciogenic methods that target ice crystals. Evidence is strongest for wintertime orographic clouds with constrained dynamics; attribution in complex clouds is difficult, and cloud-scale proof for hail cannons and ionisation remains lacking. [8]

| Question | Evidence-led answer for Guadeloupe |
| --- | --- |
| Can it create rain from blue sky | No. It can only attempt to modify suitable existing clouds. |
| Is silver used | Usually AgI for glaciogenic seeding; hygroscopic warm-cloud methods generally use salts. |
| Are rockets used | Yes in some programmes, but they bring explosives, aviation and environmental controls. |
| Is it dependable enough for the 8,000-person budget | No. Tropical variability and attribution difficulty make it research only. |
| Should equipment be purchased now | No. First commission a study with Météo-France, universities and competent French authorities, with defined success and monitoring. |

France's ANELFA network uses ground silver-iodide generators for hail suppression. That does not demonstrate reliable potable supply in Guadeloupe, and seeding would not bypass treatment, storage or compliance.

# Treatment and assurance

| Source | Main hazards | Minimum treatment concept |
| --- | --- | --- |
| Rain | Bird and animal contamination roof debris metals first flush | First flush screened opaque tank filtration validated disinfection periodic cleaning |
| Fog and dew | Airborne dust microorganisms mesh and gutter contamination | Source protection filtration validated disinfection routine chemistry and microbiology |
| Solar distillate | Volatile carryover very low mineral content storage contamination | Source exclusion activated carbon if justified remineralisation disinfection |
| RO permeate | Low alkalinity boron under some conditions post-treatment contamination | Remineralisation and pH control disinfection conductivity and lab verification |
| AWG water | Airborne contaminants wet surfaces biofilm | Air filtration sanitation programme mineral finish disinfection and microbiology |

The finished water system should be designed to the applicable French requirements implementing the EU Drinking Water Directive, with ARS Guadeloupe engagement before potable use. WHO's desalination guidance is a useful design reference, but it does not replace French authorization, surveillance and potable-contact requirements. [4] [9]

# Twelve month delivery plan

| Period | Work | Decision gate |
| --- | --- | --- |
| 0–30 days | Confirm sites and demand engage ARS and water authority issue raw-water sampling plan buy manual emergency units | Approved design basis and sampling chain |
| Month 1–3 | Install six fog test collectors twelve GWS-1 stills one commercial still comparator rain tank upgrades | Verified instruments and baseline lab results |
| Month 2–4 | Issue EU-first performance tender plus China comparison lot or alternates | Three compliant bids with comparable scope |
| Month 4–6 | Witness factory tests complete intake and brine studies finalise tank and PV civil design | FAT pass and permits pathway |
| Month 6–10 | Construct intake foundations PV 360 m³ storage install and commission RO | Site acceptance at guaranteed output and water quality |
| Month 10–12 | Optimise REFLUX loops cyclone drill audit spares review fog and still dataset | Operational readiness and scale or stop decisions |

## Pilot success criteria

| Pilot | Scale trigger | Stop or redesign trigger |
| --- | --- | --- |
| Fog | Dry-season median and 90 percent availability support target cost microbiology controllable | Cyclone handling impractical yield too intermittent contamination burden high |
| GWS-1 | At least 2.5 L/m²/day campaign average with acceptable cleaning and no leaks | Frequent glass or seal failure carryover contamination labour cost excessive |
| Solar SWRO | Guaranteed 120 m³/day service with N+1 compliant water measured whole-plant energy | Pretreatment instability missing spares brine pathway not permitted |
| AWG | Only if point-use mission values independence more than energy cost | Any proposal to substitute AWG for the 120 m³/day seawater plant |
| Brine recovery | Net extra water or saleable product with safe chemistry and positive lifecycle case | Scaling chemical accumulation no legal offtake or disposal route |

# Immediate procurement package

1.  Six standard 1 m² fog collectors with matched weather and rainfall logging.

2.  Twelve locally built GWS-1 solar stills and one complete commercial solar-still benchmark.

3.  Local ACS-compliant rain and finished-water tanks for pilots, with first-flush and disinfection components.

4.  Manual RO kits for critical response and one small DC energy-recovery watermaker for operational training.

5.  A two-stage tender for a 120 m³/day guaranteed solar SWRO service with N+1 trains, PV, intake, pretreatment, remineralisation, disinfection, split 360 m³ storage, brine management, training and two-year critical spares.

6.  An optional priced REFLUX IT side-stream package covering pressure recovery as mandatory and heat or brine recovery as separately testable pilots.

|  | Bottom line Spend the first money on measurements, local storage and emergency diversity. Spend the large money on a guaranteed modular solar SWRO service, not on an unverified atmospheric-water or cloud-seeding promise. Keep European manufacturing and Guadeloupe value creation at the centre through whole-life scoring, while letting capable Chinese vendors prove themselves against exactly the same acceptance test. |
| --- | --- |

# Sources and vendor links

Accessed 11 October 2026. Vendor capacities, efficiencies and prices are claims for screening until written into a guaranteed contract and verified at factory and site acceptance.

[1] World Health Organization  Water sanitation and hygiene guidance for emergencies  Emergency quantity planning basis.

[2] Observatoire de l'eau Guadeloupe  Cycle de l'eau et répartition de la ressource en eau en Guadeloupe  1991–2020 rainfall and windward relief effect.

[3] FogQuest  Fog collection frequently asked questions  Passive operation  mesh specification  indicative output and project costs.

[4] World Health Organization  Safe drinking-water from desalination  Health risk management  post-treatment and stability.

[5] OSMOSUN  OSMOSUN solar seawater desalination  Commercial range  battery-free operation  energy and PV sizing claims.

[6] GENAQ  Atmospheric water generator solutions  Current nominal output and energy figures.

[7] European Commission  Life-cycle costing in green public procurement  Transparent lifecycle method and tender data principles.

[8] World Meteorological Organization  WMO Statement on Weather Modification  Evidence limits and cloud-seeding distinctions.

[9] European Union  Directive EU 2020 2184 on the quality of water intended for human consumption  EU drinking-water framework.

[10] Aqualonis  CloudFisher products  Commercial fog collector family.

[11] KnitMesh Technologies  Fog collectors  Engineered fog collection media.

[12] Katadyn  Survivor desalination products  Manual emergency watermakers.

[13] Spectra Watermakers  Aquifer watermakers  Low-power DC energy-recovery watermakers.

[14] F Cubed  Carocell solar desalination  Passive solar desalination products and project claims.

[15] Elemental Water Makers  Solar desalination systems  EU commercial solar RO supplier.

[16] Solar Water Solutions  SolarRO desalination  Renewable desalination supplier.

[17] Boreal Light  Winture solar water systems  Large solar water-treatment systems.

[18] RN Solutions  Membrane distillation  Low-grade-heat membrane-distillation option.

[19] memsys  Membrane distillation systems  German thermal membrane systems.

[20] Salinity Solutions  Batch reverse osmosis  High-recovery batch RO for suitable brackish and wastewater feeds.

[21] Jiangsu Fenghai New Energy Desalinated Development  SWRO product list  Chinese 5–144 m³/day listed systems and larger ranges.

[22] Zhuhai Wangyang Water Treatment  Containerized seawater desalination  Chinese container SWRO examples.

[23] Snowate  Desalination energy recovery devices  Chinese pressure-exchanger comparison.

[24] Heaven Springs  Atmospheric water generation  Chinese AWG comparison.

[25] PROCAP  Procap water tanks  Antilles tank manufacturing and potable models.

[26] Bèl Lapli  Aqua rainwater systems  Guadeloupe rainwater installation route.